## Sheet1
编号 | 步骤 | item编号 | 检查状态 | 检查条件 | 中文描述 | 中文语音 | 英文描述 | 英文语音
m_index | m_step | m_id | m_state | m_condition | m_ch_txt | m_ch_voice | m_en_txt | m_en_voice
1 | 1 | 10016 | L |  | 变频传动器正常断电，首先通过cdp盘选择本地模式 | debug_s26_step_c_ 1 | The frequency converter gear is normally powered off. First select the local mode by cdp disk. | debug_s26_step_ce_ 1
2 | 2 | 2717 | on |  | 确认cdp盘state inu状态为readyrun，按下supplyoff按钮，断开传动单元电源，主回路断路器跳开，等到supply off指示灯常亮，cdp盘显示为readyon时拉出主回路断路器，锁定并贴上标签 | debug_s26_step_c_ 2 | Confirm the state inu status of cdp disc is readyrun， press button supplyoff to disconnect the power of the transmission unit. The main circuit breaker jumps off and when the supply off indicator light is always on and cdp disc is shown as readyon， pull out the main circuit breaker， lock and label it. | debug_s26_step_ce_ 2
3 | 2 | 10015 | ReadyOn | light
4 | 3 | 2720 | on |  | 待接地指示灯亮起，将接地开关接地，cdp屏显示DCGndN Open、NotReadyOn、INUis not ready | debug_s26_step_c_ 3 | When the earthing indicator light is on， ground the earthing switch. The cdp screen displays DCGndN Open、NotReadyOn、INUis not ready. | debug_s26_step_ce_ 3
5 | 3 | 10015 | DGGndNOpen、NotReadyOn、INUsNotRdy
6 | 4 | 2508 | off |  | 关闭综合控制箱的QF1断路器 | debug_s26_step_c_ 4 | Close the QF1 breaker of integrated control box. | debug_s26_step_ce_ 4