## Sheet1
编号 | 步骤 | item编号 | 检查状态 | 检查条件 | 中文描述 | 中文语音 | 英文描述 | 英文语音
m_index | m_step | m_id | m_state | m_condition | m_ch_txt | m_ch_voice | m_en_txt | m_en_voice
1 | 1 | 111 | on |  | 链接熔断器，查看s3屏幕上参数是否正确，电池参数电压为243伏，电流为0安，控母电压为225伏，电流为0.3安，并且控母电压表电压为243伏，直流电流为0安 | debug_s2_step_c_ 1 | Link fuse， and check the parameters on s3 screen are correct. The voltage of battery parameters is 243V and current is 0A. The master control voltage is 225V and current is 0.3A. The voltage of master control voltmeter is 243V and direct current is 0A. | debug_s2_step_ce_ 1
2 | 1 | 112 | 243
3 | 1 | 113 | 0
4 | 1 | 114 | 225
5 | 1 | 115 | 0.3
6 | 1 | 116 | 243
7 | 1 | 117 | 0
8 | 2 | 118 | on |  | 合并断路器2QF，辅助400伏电源是否得电 | debug_s2_step_c_ 2 | Combine breaker 2QF， and check whether the auxiliary 400V power is available | debug_s2_step_ce_ 2
9 | 2 | 1602 | on
10 | 2 | 1702 | on
11 | 2 | 1802 | on
12 | 2 | 2002 | on
13 | 2 | 2202 | on
14 | 3 | 120 | on |  | 合并控母电源一号，二号，三号，查看高压室开关控制柜电源是否得电 | debug_s2_step_c_ 3 | Combine the control master power source No. 1， 2 and 3， and check whether the power of the switch control cabinet in high voltage room is available | debug_s2_step_ce_ 3
15 | 3 | 121 | on
16 | 3 | 122 | on
17 | 3 | 1302 | on
18 | 3 | 1402 | on
19 | 3 | 1502 | on
20 | 4 | 124 | on |  | 合并控母电源四号，查看燃机控制柜综合测量模块是否得电 | debug_s2_step_c_ 4 | Combine the control master power No. 4， and check whether the gas turbine control cabinet comprehensive measurement module is powered on | debug_s2_step_ce_ 4
21 | 4 | 413 | on
22 | 4 | 513 | on
23 | 4 | 613 | on
24 | 4 | 713 | on
25 | 5 | 126 | on |  | 合并24伏电源断路器，查看市电及燃机控制柜进线电源是否接通 | debug_s2_step_c_ 5 | Combine 24V power breaker， and check whether the power supply in the city power supply and gas turbine control cabinet is connected | debug_s2_step_ce_ 5
26 | 5 | 305 | on
27 | 5 | 405 | on
28 | 5 | 505 | on
29 | 5 | 605 | on
30 | 5 | 705 | on